## Office
District Cooling Demand in Office
[26 empty] | Water density supply | 1000
[28 empty] | Cut-Off (kW) | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | Max R134a flow (kg/s) | 1.634
Date/Time | Measured Cooling Demand (kWh) | Flow Rate (m³) | Supply Temp (ºC) | Return Temp ºC | Storage Discharge (kW) | [16 empty] | rho*cp | Mean Water Flow rate (kg/s) | Mean R134a Flow rate (kg/s)
08-08 00 | 101.68 | 8.75 | 5 | 15.17 | 1.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.4766 | 2.4306 | 0.62005
08-08 01 | 100.95 | 8.8 | 5 | 15 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4129.7727 | 2.4444 | 0.6156
08-08 02 | 94.83 | 8.42 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.4893 | 2.3389 | 0.57828
08-08 03 | 89.92 | 8.26 | 6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4354.4794 | 2.2944 | 0.54834
08-08 04 | 84.48 | 7.82 | 6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4321.2276 | 2.1722 | 0.51517
08-08 05 | 85.48 | 7.98 | 6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4284.7118 | 2.2167 | 0.52126
08-08 06 | 91.47 | 8.64 | 5.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4011.8421 | 2.4 | 0.55779
08-08 07 | 104.95 | 10.2 | 6 | 15 | 4.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.6863 | 2.8333 | 0.63999
08-08 08 | 127.48 | 11.82 | 6 | 15.33 | 27.48 | 17.48 | 7.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4161.4572 | 3.2833 | 0.77738
08-08 09 | 147.9 | 13.25 | 6 | 16 | 47.9 | 37.9 | 27.9 | 17.9 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.4151 | 3.6806 | 0.90191
08-08 10 | 165.9 | 14.86 | 6 | 16 | 65.9 | 55.9 | 45.9 | 35.9 | 25.9 | 15.9 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4019.1117 | 4.1278 | 1.0117
08-08 11 | 181.22 | 13.27 | 4.5 | 16.67 | 81.22 | 71.22 | 61.22 | 51.22 | 41.22 | 31.22 | 21.22 | 11.22 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.6815 | 3.6861 | 1.1051
08-08 12 | 201.08 | 14.23 | 4.67 | 17 | 101.08 | 91.08 | 81.08 | 71.08 | 61.08 | 51.08 | 41.08 | 31.08 | 21.08 | 11.08 | 1.08 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.7547 | 3.9528 | 1.2262
08-08 13 | 204.32 | 15.06 | 5 | 17 | 104.32 | 94.32 | 84.32 | 74.32 | 64.32 | 54.32 | 44.32 | 34.32 | 24.32 | 14.32 | 4.32 | 0 | 0 | 0 | 0 | 0 | 0 | 4070.1195 | 4.1833 | 1.246
08-08 14 | 207.5 | 14.91 | 4.67 | 17 | 107.5 | 97.5 | 87.5 | 77.5 | 67.5 | 57.5 | 47.5 | 37.5 | 27.5 | 17.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4063.3093 | 4.1417 | 1.2654
08-08 15 | 211.23 | 14.63 | 4.67 | 17 | 111.23 | 101.23 | 91.23 | 81.23 | 71.23 | 61.23 | 51.23 | 41.23 | 31.23 | 21.23 | 11.23 | 1.23 | 0 | 0 | 0 | 0 | 0 | 4215.5156 | 4.0639 | 1.2881
08-08 16 | 201.25 | 14.95 | 5.17 | 16.83 | 101.25 | 91.25 | 81.25 | 71.25 | 61.25 | 51.25 | 41.25 | 31.25 | 21.25 | 11.25 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 4156.2211 | 4.1528 | 1.2272
08-08 17 | 204.68 | 15.03 | 5 | 17 | 104.68 | 94.68 | 84.68 | 74.68 | 64.68 | 54.68 | 44.68 | 34.68 | 24.68 | 14.68 | 4.68 | 0 | 0 | 0 | 0 | 0 | 0 | 4085.4291 | 4.175 | 1.2482
08-08 18 | 198.02 | 14.54 | 5 | 17 | 98.02 | 88.02 | 78.02 | 68.02 | 58.02 | 48.02 | 38.02 | 28.02 | 18.02 | 8.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4085.6946 | 4.0389 | 1.2075
08-08 19 | 184.88 | 12.25 | 4.83 | 17.83 | 84.88 | 74.88 | 64.88 | 54.88 | 44.88 | 34.88 | 24.88 | 14.88 | 4.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4179.3909 | 3.4028 | 1.1274
08-08 20 | 186.37 | 11.95 | 5 | 18.5 | 86.37 | 76.37 | 66.37 | 56.37 | 46.37 | 36.37 | 26.37 | 16.37 | 6.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4158.8842 | 3.3194 | 1.1365
08-08 21 | 161.17 | 11.75 | 5 | 16.67 | 61.17 | 51.17 | 41.17 | 31.17 | 21.17 | 11.17 | 1.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4231.3406 | 3.2639 | 0.98283
08-08 22 | 132.27 | 10.57 | 5 | 16 | 32.27 | 22.27 | 12.27 | 2.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4095.3986 | 2.9361 | 0.80659
08-08 23 | 114.67 | 9.67 | 5 | 15.5 | 14.67 | 4.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4065.7113 | 2.6861 | 0.69927
08-09 00 | 80.68 | 7.21 | 5 | 14.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4098.0722 | 2.0028 | 0.49199
08-09 01 | 46.42 | 4.7 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3950.6383 | 1.3056 | 0.28307
08-09 02 | 44.92 | 4.69 | 5.67 | 13.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4225.5111 | 1.3028 | 0.27393
08-09 03 | 54.37 | 3.84 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4633.8068 | 1.0667 | 0.33155
08-09 04 | 88.17 | 5.81 | 6 | 19.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4148.2167 | 1.6139 | 0.53767
08-09 05 | 67.82 | 4.69 | 6 | 18.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4222.0597 | 1.3028 | 0.41357
08-09 06 | 86.63 | 5.91 | 6 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4164.9205 | 1.6417 | 0.52828
08-09 07 | 103.55 | 6.15 | 4 | 19 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.9756 | 1.7083 | 0.63146
08-09 08 | 126.02 | 7.42 | 4 | 19 | 26.02 | 16.02 | 6.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4076.1186 | 2.0611 | 0.76848
08-09 09 | 169.23 | 10.12 | 4.33 | 19 | 69.23 | 59.23 | 49.23 | 39.23 | 29.23 | 19.23 | 9.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4103.6398 | 2.8111 | 1.032
08-09 10 | 199.22 | 12.06 | 4.67 | 19 | 99.22 | 89.22 | 79.22 | 69.22 | 59.22 | 49.22 | 39.22 | 29.22 | 19.22 | 9.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4149.9412 | 3.35 | 1.2149
08-09 11 | 240.22 | 16.64 | 5.5 | 18.5 | 140.22 | 130.22 | 120.22 | 110.22 | 100.22 | 90.22 | 80.22 | 70.22 | 60.22 | 50.22 | 40.22 | 30.22 | 20.22 | 10.22 | 0.22 | 0 | 0 | 3997.7441 | 4.6222 | 1.4649
08-09 12 | 245.78 | 16.57 | 6 | 18.67 | 145.78 | 135.78 | 125.78 | 115.78 | 105.78 | 95.78 | 85.78 | 75.78 | 65.78 | 55.78 | 45.78 | 35.78 | 25.78 | 15.78 | 5.78 | 0 | 0 | 4214.5375 | 4.6028 | 1.4988
08-09 13 | 264.53 | 16.58 | 5.17 | 19 | 164.53 | 154.53 | 144.53 | 134.53 | 124.53 | 114.53 | 104.53 | 94.53 | 84.53 | 74.53 | 64.53 | 54.53 | 44.53 | 34.53 | 24.53 | 14.53 | 4.53 | 4153.0841 | 4.6056 | 1.6131
08-09 14 | 263.2 | 16.13 | 5 | 19 | 163.2 | 153.2 | 143.2 | 133.2 | 123.2 | 113.2 | 103.2 | 93.2 | 83.2 | 73.2 | 63.2 | 53.2 | 43.2 | 33.2 | 23.2 | 13.2 | 3.2 | 4195.9082 | 4.4806 | 1.605
08-09 15 | 263.1 | 16.19 | 5 | 19 | 163.1 | 153.1 | 143.1 | 133.1 | 123.1 | 113.1 | 103.1 | 93.1 | 83.1 | 73.1 | 63.1 | 53.1 | 43.1 | 33.1 | 23.1 | 13.1 | 3.1 | 4178.77 | 4.4972 | 1.6044
08-09 16 | 267.95 | 16.48 | 5 | 19 | 167.95 | 157.95 | 147.95 | 137.95 | 127.95 | 117.95 | 107.95 | 97.95 | 87.95 | 77.95 | 67.95 | 57.95 | 47.95 | 37.95 | 27.95 | 17.95 | 7.95 | 4180.9119 | 4.5778 | 1.634
08-09 17 | 255.48 | 15.77 | 5 | 19 | 155.48 | 145.48 | 135.48 | 125.48 | 115.48 | 105.48 | 95.48 | 85.48 | 75.48 | 65.48 | 55.48 | 45.48 | 35.48 | 25.48 | 15.48 | 5.48 | 0 | 4165.8121 | 4.3806 | 1.5579
08-09 18 | 239.98 | 14.75 | 5 | 19 | 139.98 | 129.98 | 119.98 | 109.98 | 99.98 | 89.98 | 79.98 | 69.98 | 59.98 | 49.98 | 39.98 | 29.98 | 19.98 | 9.98 | 0 | 0 | 0 | 4183.6707 | 4.0972 | 1.4634
08-09 19 | 221.8 | 13.79 | 5 | 19 | 121.8 | 111.8 | 101.8 | 91.8 | 81.8 | 71.8 | 61.8 | 51.8 | 41.8 | 31.8 | 21.8 | 11.8 | 1.8 | 0 | 0 | 0 | 0 | 4135.9163 | 3.8306 | 1.3526
08-09 20 | 149.07 | 10.42 | 5 | 17.17 | 49.07 | 39.07 | 29.07 | 19.07 | 9.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4231.8908 | 2.8944 | 0.90904
08-09 21 | 91.67 | 7.21 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4161.039 | 2.0028 | 0.55901
08-09 22 | 78.37 | 6.29 | 4.5 | 15.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4203.7539 | 1.7472 | 0.47791
08-09 23 | 65.55 | 5.69 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4147.2759 | 1.5806 | 0.39973
08-10 00 | 50.78 | 4.78 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4249.3724 | 1.3278 | 0.30966
08-10 01 | 47.45 | 4.64 | 5 | 13.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4169.2701 | 1.2889 | 0.28935
08-10 02 | 47.53 | 4.68 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4062.3932 | 1.3 | 0.28984
08-10 03 | 50.98 | 4.95 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4119.596 | 1.375 | 0.31088
08-10 04 | 70.63 | 6.66 | 5 | 14.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4092.002 | 1.85 | 0.43071
08-10 05 | 67.08 | 6.48 | 5 | 14.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4063.9767 | 1.8 | 0.40906
08-10 06 | 84.9 | 7.71 | 5 | 14.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4099.4854 | 2.1417 | 0.51773
08-10 07 | 78.92 | 5.37 | 5.33 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3966.0617 | 1.4917 | 0.48126
08-10 08 | 99.08 | 6.08 | 5.33 | 19.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4091.0592 | 1.6889 | 0.6042
08-10 09 | 95.82 | 5.69 | 5 | 19.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.5326 | 1.5806 | 0.58432
08-10 10 | 123.68 | 7.09 | 3.83 | 19.17 | 23.68 | 13.68 | 3.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.8355 | 1.9694 | 0.75421
08-10 11 | 175.45 | 10.23 | 4 | 19 | 75.45 | 65.45 | 55.45 | 45.45 | 35.45 | 25.45 | 15.45 | 5.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.129 | 2.8417 | 1.0699
08-10 12 | 199.63 | 12.49 | 5 | 19 | 99.63 | 89.63 | 79.63 | 69.63 | 59.63 | 49.63 | 39.63 | 29.63 | 19.63 | 9.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4109.9623 | 3.4694 | 1.2174
08-10 13 | 227.1 | 14.07 | 5 | 19 | 127.1 | 117.1 | 107.1 | 97.1 | 87.1 | 77.1 | 67.1 | 57.1 | 47.1 | 37.1 | 27.1 | 17.1 | 7.1 | 0 | 0 | 0 | 0 | 4150.4721 | 3.9083 | 1.3849
08-10 14 | 232.6 | 14.25 | 5 | 19 | 132.6 | 122.6 | 112.6 | 102.6 | 92.6 | 82.6 | 72.6 | 62.6 | 52.6 | 42.6 | 32.6 | 22.6 | 12.6 | 2.6 | 0 | 0 | 0 | 4197.2932 | 3.9583 | 1.4184
08-10 15 | 234.47 | 14.41 | 5 | 19 | 134.47 | 124.47 | 114.47 | 104.47 | 94.47 | 84.47 | 74.47 | 64.47 | 54.47 | 44.47 | 34.47 | 24.47 | 14.47 | 4.47 | 0 | 0 | 0 | 4184.0587 | 4.0028 | 1.4298
08-10 16 | 242.04 | 15.09 | 5 | 19 | 142.04 | 132.04 | 122.04 | 112.04 | 102.04 | 92.04 | 82.04 | 72.04 | 62.04 | 52.04 | 42.04 | 32.04 | 22.04 | 12.04 | 2.04 | 0 | 0 | 4124.5101 | 4.1917 | 1.476
08-10 17 | 226.87 | 14 | 5 | 19 | 126.87 | 116.87 | 106.87 | 96.87 | 86.87 | 76.87 | 66.87 | 56.87 | 46.87 | 36.87 | 26.87 | 16.87 | 6.87 | 0 | 0 | 0 | 0 | 4167 | 3.8889 | 1.3835
08-10 18 | 196.33 | 12.19 | 5 | 19 | 96.33 | 86.33 | 76.33 | 66.33 | 56.33 | 46.33 | 36.33 | 26.33 | 16.33 | 6.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.4977 | 3.3861 | 1.1972
08-10 19 | 182.35 | 11.39 | 5 | 19 | 82.35 | 72.35 | 62.35 | 52.35 | 42.35 | 32.35 | 22.35 | 12.35 | 2.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.7691 | 3.1639 | 1.112
08-10 20 | 130.97 | 9.57 | 5 | 16.67 | 30.97 | 20.97 | 10.97 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4221.7405 | 2.6583 | 0.79867
08-10 21 | 80.8 | 6.65 | 5 | 15.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4301.018 | 1.8472 | 0.49272
08-10 22 | 72.85 | 6.05 | 4.83 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4262.415 | 1.6806 | 0.44425
08-10 23 | 62.87 | 5.6 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4041.6429 | 1.5556 | 0.38339
08-13 00 | 34.47 | 2.25 | 5 | 18.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4187.6993 | 0.625 | 0.2102
08-13 01 | 41.88 | 2.81 | 5.5 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4073.963 | 0.78056 | 0.25539
08-13 02 | 38.03 | 2.73 | 6 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3958.1255 | 0.75833 | 0.23191
08-13 03 | 45.45 | 3.02 | 5.67 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4167.6006 | 0.83889 | 0.27716
08-13 04 | 53.38 | 3.59 | 5 | 18.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4015.6557 | 0.99722 | 0.32552
08-13 05 | 53.98 | 3.84 | 6 | 18.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4104.3187 | 1.0667 | 0.32917
08-13 06 | 45.18 | 3 | 5.83 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.6287 | 0.83333 | 0.27551
08-13 07 | 61.67 | 4.58 | 6.83 | 18.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.5197 | 1.2722 | 0.37607
08-13 08 | 63.83 | 4.11 | 6 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.4436 | 1.1417 | 0.38924
08-13 09 | 72.58 | 4.62 | 6 | 19.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4089.3597 | 1.2833 | 0.4426
08-13 10 | 78.35 | 4.99 | 6 | 19.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4134.9707 | 1.3861 | 0.47778
08-13 11 | 75.58 | 4.35 | 4.83 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.2014 | 1.2083 | 0.46089
08-13 12 | 87.53 | 4.95 | 4.33 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4062.4239 | 1.375 | 0.53377
08-13 13 | 78.5 | 4.74 | 5.17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.2463 | 1.3167 | 0.4787
08-13 14 | 103.25 | 6.3 | 5 | 19.67 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.8132 | 1.75 | 0.62963
08-13 15 | 123.32 | 7.73 | 5 | 19.17 | 23.32 | 13.32 | 3.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.094 | 2.1472 | 0.75202
08-13 16 | 115.07 | 7.26 | 5 | 19.17 | 15.07 | 5.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4026.7822 | 2.0167 | 0.70171
08-13 17 | 86.85 | 5.37 | 5 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4015.4113 | 1.4917 | 0.52962
08-13 18 | 71.67 | 4.38 | 5 | 19.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3972.1409 | 1.2167 | 0.43705
08-13 19 | 65.35 | 4.12 | 5.33 | 19.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.8628 | 1.1444 | 0.39851
08-13 20 | 47.22 | 3.06 | 5.67 | 18.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4221.3481 | 0.85 | 0.28795
08-13 21 | 48.87 | 3.18 | 6 | 19.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4200.7994 | 0.88333 | 0.29801
08-13 22 | 51.9 | 3.41 | 6 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.753 | 0.94722 | 0.31649
08-13 23 | 44.58 | 2.99 | 6 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.8397 | 0.83056 | 0.27185
08-14 00 | 23.23 | 1.71 | 6 | 18.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.5097 | 0.475 | 0.14166
08-14 01 | 33.12 | 2.41 | 6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.8216 | 0.66944 | 0.20197
08-14 02 | 29.77 | 1.91 | 6 | 18.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4550.7701 | 0.53056 | 0.18154
08-14 03 | 35.57 | 2.48 | 6 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.7097 | 0.68889 | 0.21691
08-14 04 | 19.95 | 1.45 | 6 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3962.4828 | 0.40278 | 0.12166
08-14 05 | 41.4 | 2.83 | 5.83 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4156.6149 | 0.78611 | 0.25246
08-14 06 | 28.78 | 1.97 | 4.83 | 17.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4096.0197 | 0.54722 | 0.1755
08-14 07 | 48.27 | 2.96 | 4 | 18.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4096.773 | 0.82222 | 0.29435
08-14 08 | 48.97 | 2.91 | 4 | 18.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4085.0602 | 0.80833 | 0.29862
08-14 09 | 54.12 | 3.21 | 4 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.3774 | 0.89167 | 0.33003
08-14 10 | 60.48 | 3.59 | 4 | 18.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4134.1832 | 0.99722 | 0.36881
08-14 11 | 85.53 | 6.19 | 4 | 15.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4204.8023 | 1.7194 | 0.52157
08-14 12 | 75.97 | 5.94 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4185.6749 | 1.65 | 0.46327
08-14 13 | 79.95 | 6.16 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4247.6387 | 1.7111 | 0.48754
08-14 14 | 77.4 | 6.02 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4207.7922 | 1.6722 | 0.47199
08-14 15 | 84.12 | 6.38 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4315.0755 | 1.7722 | 0.51297
08-14 16 | 61.58 | 5.06 | 4 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4172.5579 | 1.4056 | 0.37552
08-14 17 | 63.67 | 5.21 | 4 | 14.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4258.9183 | 1.4472 | 0.38826
08-14 18 | 61.82 | 5.08 | 4 | 14.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4240.9921 | 1.4111 | 0.37698
08-14 19 | 60.87 | 5.12 | 4 | 14.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4143.1964 | 1.4222 | 0.37119
08-14 20 | 60.35 | 5.16 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4210.4651 | 1.4333 | 0.36802
08-14 21 | 53.75 | 4.63 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4179.2657 | 1.2861 | 0.32777
08-14 22 | 53.03 | 4.51 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4232.9933 | 1.2528 | 0.32338
08-14 23 | 48.93 | 4.33 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4068.0831 | 1.2028 | 0.29838
08-15 00 | 44.97 | 4 | 4 | 13.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4185.4188 | 1.1111 | 0.27423
08-15 01 | 47.83 | 4.14 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4159.1304 | 1.15 | 0.29167
08-15 02 | 43.75 | 4.32 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4050.9259 | 1.2 | 0.26679
08-15 03 | 44.52 | 5.06 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3959.2885 | 1.4056 | 0.27149
08-15 04 | 46.02 | 5.13 | 6 | 13.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.4875 | 1.425 | 0.28063
08-15 05 | 45.32 | 4.25 | 4.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.9164 | 1.1806 | 0.27637
08-15 06 | 43.48 | 3.88 | 4 | 13.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4103.9947 | 1.0778 | 0.26514
08-15 07 | 46.57 | 4.06 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4129.3596 | 1.1278 | 0.28399
08-15 08 | 47.12 | 4.06 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4178.1281 | 1.1278 | 0.28734
08-15 09 | 54.62 | 4.7 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4183.6596 | 1.3056 | 0.33308
08-15 10 | 58.48 | 4.97 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4235.9759 | 1.3806 | 0.35662
08-15 11 | 54.58 | 4.69 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4189.5096 | 1.3028 | 0.33283
08-15 12 | 56.6 | 4.79 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4253.8622 | 1.3306 | 0.34515
08-15 13 | 73.25 | 5.94 | 4 | 14.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4160.6316 | 1.65 | 0.44668
08-15 14 | 98.08 | 7.36 | 4 | 15.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4294.8893 | 2.0444 | 0.5981
08-15 15 | 114.05 | 9.34 | 5 | 15.83 | 14.05 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4059.0318 | 2.5944 | 0.69549
08-15 16 | 120.2 | 10.76 | 6 | 15.67 | 20.2 | 10.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4158.8018 | 2.9889 | 0.73299
08-15 17 | 113.92 | 10.56 | 6 | 15.17 | 13.92 | 3.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4235.1542 | 2.9333 | 0.69469
08-15 18 | 107.73 | 10.13 | 6 | 15 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4253.8993 | 2.8139 | 0.65695
08-15 19 | 104.13 | 10.02 | 6 | 15 | 4.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4156.8862 | 2.7833 | 0.63499
08-15 20 | 84.02 | 9.17 | 6.83 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4300.5151 | 2.5472 | 0.51236
08-15 21 | 61.42 | 6.63 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168.7783 | 1.8417 | 0.37454
08-15 22 | 57.22 | 6.29 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.6407 | 1.7472 | 0.34893
08-15 23 | 53.12 | 6.11 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3912.275 | 1.6972 | 0.32393

## Thermodynamics
Working fluid | R134a
Coefficient of performance | 2.4 | [-] | 1-s2.0-S1290072909000799-main.pdf
Storage Temperature T_st | -11 | [°C]
Evaporator Temperature T_ch | -12 | [°C]
Storage density | 167.4 | [MJ/m3]
Discharge temperature T_dc | 2 | [°C]
Ambient Temp T_0 | 20 | [°C]
Point 1 |  |  | Point 2
Pressure [kPa] | 185.2 |  | Pressure [kPa] | 571.7
Temperature [°C] | -12 |  | Temperature [°C] | 25 | from https://irc.wisc.edu/properties/
Enthalpy [kJ/kg] | 243.31 |  | Enthalpy [kJ/kg] | 267
Entropy [kJ/kgK] | 0.93918 |  | Entropy [kJ/kgK] | 0.93918
Quality [-] | 1 |  | Quality [-]
Point 3 |  |  | Point 4
Pressure [kPa] | 571.7 |  | Pressure [kPa]
Temperature [°C] | 20 |  | Temperature [°C] | -12
Enthalpy [kJ/kg] | 79.324 |  | Enthalpy [kJ/kg] | 79.324
Entropy [kJ/kgK] | 0.92243 |  | Entropy [kJ/kgK]
Quality [-] | 0 |  | Quality [-]
Max R134a mass flow | 1.634 | kg/s
Q_evap (4->1) | 267.95 | kW
W_compressor | 111.6458 | kW
Q_cond (3->2) | 306.659 | kW

## Costs
Power of the compressor
Efficiency of compressor
Volume of Ice Storage
Area of evaporator
Flow rate of refrigerant
Area of condenser
Heat flow chiller
Installation Costs [$]
Pump | 0
Ice Storage Tank
Evaporator | 0
Compressor
| Storage Volume | Storage Cost [€/m3]
| 1 | 7229.6804
| 2 | 4845.0174
| 3 | 3856.2722
| 4 | 3288.6002
| 5 | 2911.0777
| 6 | 2637.7582
| 7 | 2428.5769
| 8 | 2262.0779
| 9 | 2125.6252
| 10 | 2011.2419
| 11 | 1913.6173
| 12 | 1829.0643
| 13 | 1754.9337
| 14 | 1689.2682
| 15 | 1630.5862
| 16 | 1577.7438
| 17 | 1529.842
| 18 | 1486.1631
| 19 | 1446.127
| 20 | 1409.2583
| 21 | 1375.1642
| 22 | 1343.5163
| 23 | 1314.0378
| 24 | 1286.4939
| 25 | 1260.6835
| 26 | 1236.4336
| 27 | 1213.5943
| 28 | 1192.035
| 29 | 1171.6413
| 30 | 1152.3126
| 31 | 1133.9601
| 32 | 1116.5048
| 33 | 1099.8764
| 34 | 1084.0121
| 35 | 1068.8555
| 36 | 1054.3559
| 37 | 1040.4673
| 38 | 1027.1484
| 39 | 1014.3615
| 40 | 1002.0723
| 41 | 990.2495
| 42 | 978.8645
| 43 | 967.8911
| 44 | 957.3052
| 45 | 947.0846
| 46 | 937.209
| 47 | 927.6594
| 48 | 918.4184
| 49 | 909.4698
| 50 | 900.7986
| 51 | 892.3907
| 52 | 884.2332
| 53 | 876.314
| 54 | 868.6218
| 55 | 861.1458
| 56 | 853.8763
| 57 | 846.804
| 58 | 839.9201
| 59 | 833.2164
| 60 | 826.6852
| 61 | 820.3193
| 62 | 814.1119
| 63 | 808.0565
| 64 | 802.147
| 65 | 796.3777

## Foglio7
P=0.50 MPa (15.7°C) |  |  |  | P=0.60 MPa (21.6°C)
Temp | volume | enthalpy | entropy | Temp | volume | enthalpy | entropy
°C | v(m^3/kg) | h(kJ/kg) | s(kJ/kg.K) | °C | v(m^3/kg) | h(kJ/kg) | s(kJ/kg.K)
Sat. | 0.0411 | 259.3 | 0.924 | Sat. | 0.0343 | 262.43 | 0.922
20 | 0.0421 | 263.5 | 0.938 | 30 | 0.036 | 270.8 | 0.95
30 | 0.0443 | 273 | 0.97 | 40 | 0.0379 | 280.6 | 0.982
40 | 0.0465 | 282.5 | 1.001 | 50 | 0.0397 | 290.3 | 1.012
50 | 0.0485 | 292 | 1.031 | 60 | 0.0414 | 300 | 1.042
60 | 0.0505 | 301.5 | 1.06 | 70 | 0.0431 | 309.7 | 1.071
70 | 0.0524 | 311.1 | 1.088 | 80 | 0.0447 | 319.6 | 1.099
80 | 0.0543 | 320.8 | 1.116 | 90 | 0.0463 | 329.5 | 1.126
90 | 0.0562 | 330.6 | 1.144 | 100 | 0.0479 | 339.5 | 1.154
100 | 0.0583 | 340.5 | 1.171 | 110 | 0.0495 | 349.6 | 1.18
110 | 0.06 | 350.6 | 1.197 | 120 | 0.051 | 359.8 | 1.207
120 | 0.0617 | 360.7 | 1.223 | 130 | 0.0525 | 370.2 | 1.233
130 | 0.0635 | 371 | 1.249 | 140 | 0.054 | 380.7 | 1.258
140 | 0.0653 | 381.5 | 1.275

## Electricity Prices
Price [€/MWh]
136.01 | Data from 21.10 to 36.10 Nordpool SE3
136.03
144.86
140.48
150
164.59
270.4
316.94
324.05
308.15
296.18
307.53
299.82
302.32
332.02
333.69
334.68
335.39
315.41
291.43
252.17
220
199.93
155.03
122.19
112.45
99.97
84.6
90.71
104.76
152.18
224.4
242.99
209.32
214.04
224.13
212.93
211.87
209.07
224.68
212.05
219.06
193.79
181.19
156.18
153.17
149.92
137.52
127.45
123.8
109.59
107.07
113.88
120.27
139.99
149.9
165.79
170.62
172.74
166.77
162.64
161.14
175.76
179.91
186.16
218.13
165.81
154.8
139.97
125.11
125.38
113.78
138.23
124.31
121.92
117.49
125.92
149.88
207.39
293.16
309.09
294.94
295.02
289.9
272.93
269.92
272.24
300.36
315.05
322.72
299.59
285.91
261.56
229.94
217.1
173.64
187.29
175.19
163.07
151.82
159.15
177.28
225.06
297.07
307.65
282.9
280.45
263.47
256.03
272.43
290.17
318.36
327.36
349.9
337.95
314.37
274.15
259.93
249.91
199.97
207.67
205.64
194.36
195.2
193.24
202.95
196.6
189.96
210
273.18
257.83
253.32
249.99
237.41
257.61
264.02
288.2
315.92
306.1
270.08
232.22
208.25
195.2
169.52

## Temp_Sat
R134a - TetraFlouroEthane Saturation Properties - Temperature Table
Temp | Pressure | volume (m^3/kg) |  | energy (kJ/kg) |  | enthalpy (kJ/kg) |  |  | entropy (kJ/kg.K)
deg C | kPa | vf | vg | uf | ug | hf | hfg | hg | sf | sfg | sg
-40 | 51.2 | 0.00070537 | 0.36108 | -0.036121 | 207.37 | -5.5648e-15 | 225.86 | 225.86 | -1.3023e-17 | 0.96873 | 0.96873
-36 | 62.9 | 0.0007112 | 0.29771 | 4.9922 | 209.66 | 5.0369 | 223.3531 | 228.39 | 0.021385 | 0.94183 | 0.96322
-32 | 76.7 | 0.00071719 | 0.24727 | 10.048 | 211.96 | 10.103 | 220.817 | 230.92 | 0.042529 | 0.91567 | 0.9582
-28 | 92.7 | 0.00072336 | 0.2068 | 15.133 | 214.26 | 15.2 | 218.23 | 233.43 | 0.063445 | 0.89019 | 0.95363
-26 | 101.7 | 0.0007265 | 0.18958 | 17.687 | 215.41 | 17.761 | 216.919 | 234.68 | 0.07382 | 0.87769 | 0.95151
-24 | 111.3 | 0.0007297 | 0.17407 | 20.248 | 216.55 | 20.329 | 215.601 | 235.93 | 0.084143 | 0.86534 | 0.94948
-22 | 121.7 | 0.00073294 | 0.16006 | 22.817 | 217.7 | 22.906 | 214.264 | 237.17 | 0.094414 | 0.85314 | 0.94755
-20 | 132.7 | 0.00073623 | 0.14739 | 25.394 | 218.85 | 25.492 | 212.918 | 238.41 | 0.10464 | 0.84107 | 0.94571
-18 | 144.6 | 0.00073958 | 0.13592 | 27.979 | 219.99 | 28.086 | 211.554 | 239.64 | 0.11481 | 0.82915 | 0.94396
-16 | 157.3 | 0.00074297 | 0.12551 | 30.572 | 221.13 | 30.689 | 210.181 | 240.87 | 0.12493 | 0.81736 | 0.94229
-14 | 170.8 | 0.00074643 | 0.11605 | 33.173 | 222.27 | 33.301 | 208.789 | 242.09 | 0.13501 | 0.80569 | 0.9407
-12 | 185.2 | 0.00074994 | 0.10744 | 35.783 | 223.41 | 35.922 | 207.388 | 243.31 | 0.14505 | 0.79413 | 0.93918
-10 | 200.6 | 0.00075351 | 0.09959 | 38.401 | 224.54 | 38.553 | 205.967 | 244.52 | 0.15504 | 0.7827 | 0.93774
-8 | 216.9 | 0.00075714 | 0.092422 | 41.029 | 225.67 | 41.193 | 204.527 | 245.72 | 0.16499 | 0.77137 | 0.93636
-6 | 234.3 | 0.00076084 | 0.085867 | 43.665 | 226.8 | 43.843 | 203.077 | 246.92 | 0.17489 | 0.76016 | 0.93505
-4 | 252.7 | 0.0007646 | 0.079866 | 46.31 | 227.93 | 46.504 | 201.606 | 248.11 | 0.18476 | 0.74904 | 0.9338
-2 | 272.2 | 0.00076843 | 0.074362 | 48.965 | 229.05 | 49.174 | 200.116 | 249.29 | 0.19459 | 0.73802 | 0.93261
0 | 292.8 | 0.00077233 | 0.069309 | 51.63 | 230.17 | 51.856 | 198.604 | 250.46 | 0.20439 | 0.72709 | 0.93148
2 | 314.6 | 0.00077631 | 0.064663 | 54.304 | 231.28 | 54.548 | 197.072 | 251.62 | 0.21415 | 0.71624 | 0.93039
4 | 337.7 | 0.00078037 | 0.060385 | 56.988 | 232.39 | 57.252 | 195.528 | 252.78 | 0.22387 | 0.70548 | 0.92935
6 | 362 | 0.00078451 | 0.056443 | 59.683 | 233.49 | 59.967 | 193.953 | 253.92 | 0.23357 | 0.69479 | 0.92836
8 | 387.6 | 0.00078873 | 0.052804 | 62.388 | 234.58 | 62.694 | 192.356 | 255.05 | 0.24323 | 0.68418 | 0.92741
12 | 443 | 0.00079745 | 0.046332 | 67.832 | 236.76 | 68.185 | 189.105 | 257.29 | 0.26247 | 0.66316 | 0.92563
16 | 504.3 | 0.00080657 | 0.04078 | 73.32 | 238.91 | 73.727 | 185.743 | 259.47 | 0.2816 | 0.64237 | 0.92397
20 | 571.7 | 0.0008161 | 0.035997 | 78.857 | 241.02 | 79.324 | 182.276 | 261.6 | 0.30063 | 0.6218 | 0.92243
24 | 645.8 | 0.00082612 | 0.031858 | 84.445 | 243.11 | 84.979 | 178.701 | 263.68 | 0.31958 | 0.60139 | 0.92097
26 | 685.4 | 0.00083131 | 0.029998 | 87.259 | 244.13 | 87.829 | 176.871 | 264.7 | 0.32903 | 0.59123 | 0.92026
28 | 726.9 | 0.00083665 | 0.028263 | 90.087 | 245.15 | 90.695 | 174.995 | 265.69 | 0.33847 | 0.5811 | 0.91957
30 | 770.2 | 0.00084213 | 0.026642 | 92.93 | 246.16 | 93.578 | 173.092 | 266.67 | 0.34789 | 0.57099 | 0.91888
32 | 815.4 | 0.00084777 | 0.025126 | 95.787 | 247.15 | 96.479 | 171.161 | 267.64 | 0.3573 | 0.5609 | 0.9182
34 | 862.6 | 0.00085357 | 0.023708 | 98.66 | 248.13 | 99.397 | 169.183 | 268.58 | 0.3667 | 0.55082 | 0.91752
36 | 911.9 | 0.00085954 | 0.02238 | 101.55 | 249.1 | 102.33 | 167.17 | 269.5 | 0.37609 | 0.54074 | 0.91683
38 | 963.2 | 0.00086569 | 0.021135 | 104.46 | 250.05 | 105.29 | 165.12 | 270.41 | 0.38548 | 0.53067 | 0.91615
40 | 1016.6 | 0.00087204 | 0.019966 | 107.38 | 250.99 | 108.27 | 163.01 | 271.28 | 0.39487 | 0.52058 | 0.91545
42 | 1072.2 | 0.00087859 | 0.018868 | 110.32 | 251.91 | 111.26 | 160.88 | 272.14 | 0.40425 | 0.51048 | 0.91473
44 | 1130.1 | 0.00088537 | 0.017837 | 113.28 | 252.81 | 114.28 | 158.69 | 272.97 | 0.41364 | 0.50036 | 0.914
48 | 1252.9 | 0.00089965 | 0.015951 | 119.26 | 254.56 | 120.39 | 154.16 | 274.55 | 0.43243 | 0.48003 | 0.91246
52 | 1385.4 | 0.00091502 | 0.014276 | 125.33 | 256.23 | 126.6 | 149.41 | 276.01 | 0.45127 | 0.45951 | 0.91078
56 | 1528.2 | 0.00093166 | 0.012782 | 131.49 | 257.79 | 132.92 | 144.4 | 277.32 | 0.47018 | 0.43874 | 0.90892
60 | 1681.8 | 0.00094979 | 0.011444 | 137.76 | 259.24 | 139.36 | 139.13 | 278.49 | 0.48921 | 0.4176 | 0.90681
70 | 2116.8 | 0.0010038 | 0.0086527 | 154.01 | 262.19 | 156.14 | 124.37 | 280.51 | 0.53757 | 0.36242 | 0.89999
80 | 2633.2 | 0.0010773 | 0.0064483 | 171.41 | 263.69 | 174.25 | 106.42 | 280.67 | 0.58803 | 0.30135 | 0.88938
90 | 3244.2 | 0.0011936 | 0.0046134 | 190.91 | 262.3 | 194.78 | 82.49 | 277.27 | 0.64342 | 0.22715 | 0.87057
100 | 3972.4 | 0.0015357 | 0.0026809 | 219.05 | 248.89 | 225.15 | 34.39 | 259.54 | 0.72317 | 0.09214 | 0.81531
101.06 | 4059.1 | 0.0019535 | 0.0019535 | 233.57 | 233.57 | 241.49 | 0 | 241.49 | 0.76649 | 0 | 0.76649
| (Source of table data: |  |  | NIST Chemistry WebBook |  |  | Accessed: Jan 2008)

## Press_Sat
R134a - TetraFlouroEthane Saturation Properties - Pressure Table
Pressure | Temp | volume (m^3/kg) |  | energy (kJ/kg) |  | enthalpy (kJ/kg) |  |  | entropy (kJ/kg.K)
kPa | deg C | vf | vg | uf | ug | hf | hfg | hg | sf | sfg | sg
60 | -36.935 | 0.00070982 | 0.31123 | 3.8148 | 209.13 | 3.8574 | 223.9426 | 227.8 | 0.01641 | 0.94805 | 0.96446
80 | -31.115 | 0.00071854 | 0.23755 | 11.17 | 212.47 | 11.228 | 220.242 | 231.47 | 0.047174 | 0.90998 | 0.95715
100 | -26.361 | 0.00072593 | 0.19256 | 17.225 | 215.2 | 17.298 | 217.162 | 234.46 | 0.071951 | 0.87993 | 0.95188
120 | -22.31 | 0.00073244 | 0.16214 | 22.419 | 217.52 | 22.507 | 214.473 | 236.98 | 0.092828 | 0.85501 | 0.94784
140 | -18.76 | 0.0007383 | 0.14015 | 26.996 | 219.56 | 27.1 | 212.08 | 239.18 | 0.11095 | 0.83367 | 0.94462
160 | -15.588 | 0.00074368 | 0.12349 | 31.107 | 221.37 | 31.226 | 209.894 | 241.12 | 0.12701 | 0.81495 | 0.94196
180 | -12.712 | 0.00074868 | 0.11042 | 34.852 | 223 | 34.987 | 207.893 | 242.88 | 0.14148 | 0.79824 | 0.93972
200 | -10.076 | 0.00075337 | 0.099877 | 38.301 | 224.5 | 38.452 | 206.018 | 244.47 | 0.15466 | 0.78313 | 0.93779
220 | -7.6377 | 0.0007578 | 0.091191 | 41.506 | 225.88 | 41.672 | 204.268 | 245.94 | 0.16678 | 0.76934 | 0.93612
240 | -5.3653 | 0.00076202 | 0.083906 | 44.503 | 227.16 | 44.686 | 202.614 | 247.3 | 0.17803 | 0.75662 | 0.93465
260 | -3.235 | 0.00076606 | 0.077704 | 47.325 | 228.36 | 47.524 | 201.036 | 248.56 | 0.18853 | 0.74481 | 0.93334
280 | -1.2277 | 0.00076993 | 0.07236 | 49.993 | 229.48 | 50.209 | 199.531 | 249.74 | 0.19838 | 0.73379 | 0.93217
300 | 0.67206 | 0.00077366 | 0.067704 | 52.527 | 230.54 | 52.759 | 198.091 | 250.85 | 0.20767 | 0.72343 | 0.9311
320 | 2.4768 | 0.00077727 | 0.063611 | 54.943 | 231.54 | 55.192 | 196.708 | 251.9 | 0.21647 | 0.71367 | 0.93014
340 | 4.1969 | 0.00078077 | 0.059983 | 57.253 | 232.49 | 57.519 | 195.371 | 252.89 | 0.22483 | 0.70442 | 0.92925
360 | 5.8412 | 0.00078418 | 0.056744 | 59.469 | 233.4 | 59.751 | 194.079 | 253.83 | 0.2328 | 0.69564 | 0.92844
400 | 8.9306 | 0.00079073 | 0.051207 | 63.651 | 235.09 | 63.967 | 191.613 | 255.58 | 0.24771 | 0.67927 | 0.92698
500 | 15.735 | 0.00080595 | 0.041123 | 72.955 | 238.77 | 73.358 | 185.972 | 259.33 | 0.28033 | 0.64375 | 0.92408
600 | 21.572 | 0.00081998 | 0.0343 | 81.046 | 241.85 | 81.538 | 180.892 | 262.43 | 0.30809 | 0.61376 | 0.92185
700 | 26.713 | 0.0008332 | 0.029365 | 88.266 | 244.5 | 88.849 | 176.201 | 265.05 | 0.3324 | 0.58761 | 0.92001
800 | 31.327 | 0.00084585 | 0.025625 | 94.825 | 246.82 | 95.501 | 171.819 | 267.32 | 0.35414 | 0.56429 | 0.91843
900 | 35.526 | 0.00085811 | 0.022687 | 100.86 | 248.87 | 101.64 | 167.65 | 269.29 | 0.37387 | 0.54313 | 0.917
1000 | 39.388 | 0.00087007 | 0.020316 | 106.48 | 250.7 | 107.35 | 163.67 | 271.02 | 0.39199 | 0.52367 | 0.91566
1200 | 46.315 | 0.00089351 | 0.016718 | 116.73 | 253.84 | 117.8 | 156.1 | 273.9 | 0.42451 | 0.48861 | 0.91312
1400 | 52.422 | 0.00091671 | 0.01411 | 125.97 | 256.4 | 127.26 | 148.89 | 276.15 | 0.45326 | 0.45733 | 0.91059
1600 | 57.906 | 0.0009401 | 0.012126 | 134.47 | 258.5 | 135.97 | 141.93 | 277.9 | 0.47923 | 0.42872 | 0.90795
1800 | 62.895 | 0.000964 | 0.010562 | 142.38 | 260.2 | 144.11 | 135.1 | 279.21 | 0.50307 | 0.40203 | 0.9051
2000 | 67.481 | 0.00098877 | 0.0092915 | 149.83 | 261.55 | 151.81 | 128.33 | 280.14 | 0.52524 | 0.37674 | 0.90198
2500 | 77.577 | 0.0010569 | 0.0069403 | 167.06 | 263.51 | 169.7 | 111.16 | 280.86 | 0.57551 | 0.31695 | 0.89246
3000 | 86.203 | 0.0011413 | 0.0052813 | 183.14 | 263.35 | 186.56 | 92.63 | 279.19 | 0.62145 | 0.25778 | 0.87923
| (Source of table data: | energy (kJ/kg) uf: NIST Chemistry WebBook; enthalpy (kJ/kg) hfg: Accessed: Jan 2008)